## History
* 축약어 참고 MOCSAbbreviations.xlsx
Ver | Date | Description
R0.04 | 26.03.31 | 1. Multi_MOCS_IO_List_R0.05.xlsx 반영 2. System Unit 추가 (Option 별 Alarm on/off) 3. No.# Chamber Diff. Press Low Threshold 0.5mbar, Time delay 300s 4. No#.HD Sheet Index 63~67, Venting & Sealing Air Inlet Press HW Tag 변경: PT105#50 -> PT105#50 5. No#.HD Sheet Index 78~82, No.# RTV Diff. Press Alarm 삭제 6. MOCS Ready 항목에 대한 Alarm 반영 - Common.UD Sheet Index 2-3 - No#.HD Sheet Index 22-24 7. No.# S-trap lifetime remaining Alarm 임시 반영 - No#.HD Sheet Index 25-26

## Alarm 분류
* B&R Structure | [11 empty] | * HMI Tag
|  | Unit |  | Type |  | Category1 |  | Category2 | Tag |  | Description | Alarm Tag 규칙
Alarm | . | Common | . | HD[0..74] | . |  |  | MF | HD |  | Hardware Defendant Alarm | Unit_ItemTag_Category2
[5 empty] | . | DI | . | DH | UD |  | User Defind Alarm | Examples | COM_PT102040_HH, NO2_2DI1_MF, NO3_TC106340_HH, NO4_TMBTO_FL
[7 empty] | . | DL | HD | MF | Module Fault Alarm, Alerts when the HW module is not initialized/recognized | Expression | Description | Examples
[5 empty] | . | AI | . | SF |  | AI | Analog Input | Alarm Unit
[7 empty] | . | HH |  | DI | Digital Input | COM | Common | Com_*
[7 empty] | . | HO | DI | DH | High Alarm, For the normal open(False) signal, alert when the signal is True | NO# | Individual, No1-8 | No1_*, No2_*, ... No8_*
[7 empty] | . | LO |  | DL | AlIndivUD_typ | ItemTag
[7 empty] | . | LL | AI | SF | Sensor Fault Alarm, Alert when the current falls below 3.2mA or exceed 20.16mA | ModuleTag_* | Module Fault Alarm | *_1CDI1_*, *_3AI2_*
|  |  | . | UD[0] | . |  |  | ED |  | HH | High-High Alarm, Alert when the value exceed the High-High threshold | DITag | Digital Input | *_FSP00-301_*, *_1CDI1CH15_*
[5 empty] | . |  |  | FL |  | HO | High Alarm, Alert when the value exceed the High threshold | AITag | Analog Input | *_PT102040_*, *_TC106340_*, *_3AI2CH3_*
| . | No# | . | HD[0..157] | . |  |  | MF |  | LO | Low Alarm, Alert when the value falls below the Low threshold | ErrorTag | Error or Deviation Alarm | *_DFODEV_*
[5 empty] | . | DI | . | DH |  | LL | Low-Low Alarm, Alert when the value falls below the Low-Low threshold | FlagTag | Alert when the flag is True | *_TMBTO_*
[7 empty] | . | DL | UD | ED | Error or Deviation Alarm, Alerts when the error from the target value exceeds the threshold | Alarm Category2
[5 empty] | . | AI | . | SF |  | FL | Alert when the flag is True, The Flags are processed and transmitted in Logic Level | MF | Module Fault Alarm | *_MF
[7 empty] | . | HH |  |  |  | DH | (DI) High Alarm | *_DH
[7 empty] | . | HO |  |  |  | DL | (DI) Low Alarm | *_DL
[7 empty] | . | LO |  |  |  | SF | (AI) Sensor Fault Alarm | *_SF
[7 empty] | . | LL |  |  |  | HH | (AI) High-High Alarm | *_HH
|  |  | . | UD[0..18] | . |  |  | ED |  |  |  | HO | (AI) High Alarm | *_HO
[5 empty] | . |  |  | FL |  |  |  | LO | (AI) Low Alarm | *_LO
[12 empty] | LL | (AI) Low-Low Alarm | *_LL
[12 empty] | ED | Error or Deviation Alarm | *_ED
[12 empty] | FL | Alert when the flag is True | *_FL
Dropdown Menu
Alarm Action |  | 선택
Disengage |  | O
MOCS Shutdown |  | X
Valve Shutdown
Standby pump changeover
Init
System Unit
Module
MOCS
FODS
FODSYard
SCR

## Common.HD
IDX | Alarm Tag | Enable | HW Tag | System Unit | Message | Min | Max | Unit | Threshold | Delay | Not Ready | Action | Alarm State | Reset Button | Alarm Reset Condition | Remark
double | string | string | string | string | string | double | double | string | string | double | string | string | string | string | string | string
0 | COM_DI1_MF | O | 1CDI1 | Module | Common DI1 Module Fault | 0 | 1 | - | 1 | 0.1 |  |  | All
1 | COM_DOI1_MF | O | 1CDO1 | Module | Common DO1 Module Fault | 0 | 1 | - | 1 | 0.1 |  |  | All
2 | COM_AI1_MF | O | 1CAI1 | Module | Common AI1 Module Fault | 0 | 1 | - | 1 | 0.1 |  |  | All
3 | COM_AO1_MF | O | 1CAO1 | Module | Common AO1 Module Fault | 0 | 1 | - | 1 | 0.1 |  |  | All
4 |  | X |  |  | 1CDI1 CH1 Reserved High(High=Running) | 0 | 1 | - | 1 | 0.1 | X |  | All
5 |  | X |  |  | 1CDI1 CH1 Reserved Low(High=Running) | 0 | 1 | - | 0 | 0.1 | X |  | All
6 | COM_MOC00-370_DH | X | MOC00-370 | MOCS | Alarm Reset High(High=Reset) | 0 | 1 | - | 1 | 0.1 | X |  | All
7 | COM_MOC00-370_DL | X | MOC00-370 | MOCS | Alarm Reset Low(High=Reset) | 0 | 1 | - | 0 | 0.1 | X |  | All
8 | COM_ENG10-700_DH | X | ENG10-700 | MOCS | Low Sulfur fuel supplied (S=0.1%) High(High=0.1% Sulfur) | 0 | 1 | - | 1 | 0.1 | X |  | All
9 | COM_ENG10-700_DL | O | ENG10-700 | MOCS | Low Sulfur Fuel Supplied Fail while the MOCS is working | 0 | 1 | - | 0 | 0.1 | O | MOCS Shutdown | MOCS Engage MOCS Active | O
10 | COM_MOC00-803_DH | X | MOC00-803 | MOCS | Internal power Fail High(Low=Fail) | 0 | 1 | - | 1 | 0.1 |  |  | All
11 | COM_MOC00-803_DL | O | MOC00-803 | MOCS | Internal power Fail Low(Low=Fail) | 0 | 1 | - | 0 | 0.1 |  |  | All
12 | COM_MOC00-804_DH | X | MOC00-804 | MOCS | External power Fail High(Low=Fail) | 0 | 1 | - | 1 | 0.1 |  |  | All
13 | COM_MOC00-804_DL | O | MOC00-804 | MOCS | External power Fail Low(Low=Fail) | 0 | 1 | - | 0 | 0.1 |  |  | All
14 | COM_MOC00-805_DH | X | MOC00-805 | MOCS | Fan power Fail High(Low=Fail) | 0 | 1 | - | 1 | 0.1 |  |  | All
15 | COM_MOC00-805_DL | O | MOC00-805 | MOCS | Fan power Fail Low(Low=Fail) | 0 | 1 | - | 0 | 0.1 |  |  | All
16 | COM_MOC00-806_DH | X | MOC00-806 | MOCS | ESD circuit power Fail High(Low=Fail) | 0 | 1 | - | 1 | 0.1 |  |  | All
17 | COM_MOC00-806_DL | O | MOC00-806 | MOCS | ESD circuit power Fail Low(Low=Fail) | 0 | 1 | - | 0 | 0.1 |  |  | All
18 | COM_MOC00-807_DH | X | MOC00-807 | MOCS | UPS power Fail High(Low=Fail) | 0 | 1 | - | 1 | 1 |  |  | All
19 | COM_MOC00-807_DL | O | MOC00-807 | MOCS | UPS power Fail Low(Low=Fail) | 0 | 1 | - | 0 | 1 |  |  | All
20 | COM_FSP00-201_DH | X | FSP00-201 | FODS | No.1 F.O. Supply pump Remote High(High=Remote) | 0 | 1 | - | 1 | 1 |  |  | All
21 | COM_FSP00-201_DL | O | FSP00-201 | FODS | No.1 F.O. Supply pump Remote Low(High=Remote) | 0 | 1 | - | 0 | 1 |  | Standby pump changeover | All
22 | COM_FSP00-301_DH | X | FSP00-301 | FODS | No.1 F.O. Supply pump Abnormal High(Low=Abnormal) | 0 | 1 | - | 1 | 1 |  |  | All
23 | COM_FSP00-301_DL | O | FSP00-301 | FODS | No.1 F.O. Supply pump Abnormal Low(Low=Abnormal) | 0 | 1 | - | 0 | 1 |  | Standby pump changeover | All
24 | COM_FSP00-221_DH | X | FSP00-221 | FODS | No.1 F.O. Supply pump Running High(High=Running) | 0 | 1 | - | 1 | 10 |  |  | All
25 | COM_FSP00-221_DL | O | FSP00-221 | FODS | No.1 F.O. supply pump Fail | 0 | 1 | - | 0 | 10 |  | Standby pump changeover | No1FOSPumpRunCmd == TRUE
26 | COM_FSP00-202_DH | X | FSP00-202 | FODS | No.2 F.O. Supply pump Remote High(High=Remote) | 0 | 1 | - | 1 | 1 |  |  | All
27 | COM_FSP00-202_DL | O | FSP00-202 | FODS | No.2 F.O. Supply pump Remote Low(High=Remote) | 0 | 1 | - | 0 | 1 |  | Standby pump changeover | All
28 | COM_FSP00-302_DH | X | FSP00-302 | FODS | No.2 F.O. Supply pump Abnormal High(Low=Abnormal) | 0 | 1 | - | 1 | 1 |  |  | All
29 | COM_FSP00-302_DL | O | FSP00-302 | FODS | No.2 F.O. Supply pump Abnormal Low(Low=Abnormal) | 0 | 1 | - | 0 | 1 |  | Standby pump changeover | All
30 | COM_FSP00-222_DH | X | FSP00-222 | FODS | No.2 F.O. Supply pump Running High(High=Running) | 0 | 1 | - | 1 | 10 |  |  | All
31 | COM_FSP00-222_DL | O | FSP00-222 | FODS | No.2 F.O. supply pump Fail | 0 | 1 | - | 0 | 10 |  | Standby pump changeover | No2FOSPumpRunCmd == TRUE
32 | COM_FSU10-200_DH | X | FSU10-200 | FODSYard | MOCS F.O Supply pump Running from Yard High(High=Running) | 0 | 1 | - | 1 | 0.1 |  |  | All
33 | COM_FSU10-200_DL | O | FSU10-200 | FODSYard | F.O Supply pump Fail from Yard(High=Running) | 0 | 1 | - | 0 | 10 |  |  | FOSPumpRunRqstYard == TRUE
34 |  | X |  |  | 1CDI1 CH16 Reserved High(High=Running) | 0 | 1 | - | 1 | 0.1 |  |  | All
35 |  | X |  |  | 1CDI1 CH16 Reserved Low(High=Running) | 0 | 1 | - | 0 | 0.1 |  |  | All
36 | COM_PT102040_SF | O | PT102040 | FODS | F.O. Supply, Inlet Press S/F | -1 | 10 | bar | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
37 | COM_PT102040_LL | X | PT102040 | FODS | F.O. Supply, Inlet Press Low-Low | -1 | 10 | bar | 0 | 1 |  |  | All
38 | COM_PT102040_LO | O | PT102040 | FODS | F.O. Supply, Inlet Press Low | -1 | 10 | bar | -0.2 | 2 | O | Disengage | All |  |  | Dry pump running 방지
39 | COM_PT102040_HO | X | PT102040 | FODS | F.O. Supply, Inlet Press High | -1 | 10 | bar | 0 | 1 |  |  | All
40 | COM_PT102040_HH | X | PT102040 | FODS | F.O. Supply, Inlet Press High-High | -1 | 10 | bar | 0 | 1 |  |  | All
41 | COM_PT102041_SF | O | PT102041 | FODS | F.O. Supply, Outlet Press S/F | 0 | 16 | bar | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
42 | COM_PT102041_LL | O | PT102041 | FODS | F.O. Supply, Outlet Press Low-Low | 0 | 16 | bar | 4 | 5 |  | Standby pump changeover | Flag_FOSPumpRunning == TRUE |  |  | Flag up FLAG_NO#_FO_SUPPLY_PUMP_BRKDOWN All FO Supply Pump Breakdown 조건부 MOCS Disengage & MOCS Not Ready
43 | COM_PT102041_LO | O | PT102041 | FODS | F.O. Supply, Outlet Press Low | 0 | 16 | bar | 5 | 5 |  |  | Flag_FOSPumpRunning == TRUE
44 | COM_PT102041_HO | O | PT102041 | FODS | F.O. Supply, Outlet Press High | 0 | 16 | bar | 11 | 10 |  |  | All |  |  | Pump 고장
45 | COM_PT102041_HH | O | PT102041 | FODS | F.O. Supply, Outlet Press High-High | 0 | 16 | bar | 12 | 10 | O | Disengage | All |  |  | Pump 고장
46 |  | X |  |  | 1CAI1 CH3 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
47 |  | X |  |  | 1CAI1 CH3 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
48 |  | X |  |  | 1CAI1 CH3 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
49 |  | X |  |  | 1CAI1 CH3 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
50 |  | X |  |  | 1CAI1 CH3 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
51 |  | X |  |  | 1CAI1 CH4 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
52 |  | X |  |  | 1CAI1 CH4 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
53 |  | X |  |  | 1CAI1 CH4 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
54 |  | X |  |  | 1CAI1 CH4 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
55 |  | X |  |  | 1CAI1 CH4 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
56 |  | X |  |  | 1CAI1 CH5 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
57 |  | X |  |  | 1CAI1 CH5 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
58 |  | X |  |  | 1CAI1 CH5 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
59 |  | X |  |  | 1CAI1 CH5 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
60 |  | X |  |  | 1CAI1 CH5 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
61 |  | X |  |  | 1CAI1 CH6 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
62 |  | X |  |  | 1CAI1 CH6 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
63 |  | X |  |  | 1CAI1 CH6 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
64 |  | X |  |  | 1CAI1 CH6 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
65 |  | X |  |  | 1CAI1 CH6 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
66 |  | X |  |  | 1CAI1 CH7 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
67 |  | X |  |  | 1CAI1 CH7 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
68 |  | X |  |  | 1CAI1 CH7 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
69 |  | X |  |  | 1CAI1 CH7 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
70 |  | X |  |  | 1CAI1 CH7 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
71 |  | X |  |  | 1CAI1 CH8 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
72 |  | X |  |  | 1CAI1 CH8 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
73 |  | X |  |  | 1CAI1 CH8 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
74 |  | X |  |  | 1CAI1 CH8 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
75 |  | X |  |  | 1CAI1 CH8 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All

## Common.UD
IDX | Alarm Tag | Enable | HW Tag | System Unit | Message | Min | Max | Unit | Threshold | Delay | Not Ready | Action | Alarm State | Reset Button | Alarm Reset Condition | Flag | Remark
double | string | string | string | string | string | double | double | string | string | double | string | string | string | string | string | string | string
0 | COM_COMMAMS_FL |  |  | MOCS | Communication Fail between AMS and MOCS | 0 | 1 | - | 0 | 1 | O | MOCS Shutdown | All |  |  | Flag_AMSHbeatFail == TRUE | Alert when the AMS heartbeat(n) = AMS heartbeat(n-1)
1 | COM_COMMHMI_FL |  |  | MOCS | Communication Fail between HMI and MOCS | 0 | 1 | - | 0 | 1 | X |  | All |  |  | Flag_HMIHbeatFail == TRUE | Alert when the HMI heartbeat(n) = HMI heartbeat(n-1)
2 | COM_NRDLOWS_FL | O | ENG10-700 | FODS | MOCS Not Ready - Low Sulfur Fuel Supplied Fail | 0 | 1 | - | 0 | 0.1 | O |  | Init Sealing |  | Flag_MOCSReady == TRUE | Flag_MOCSStartCmd == TRUE LowSulfFOSupd == FALSE | Flag_MOCSStartCmd == or(Flag_GE#MOCSStartCmd)
3 | COM_NRDFODP_FL | O |  | FODS | MOCS Not Ready - F.O. Supply Pump Fail | 0 | 1 | - | 0 | 0.1 | O |  | Init Sealing |  | Flag_MOCSReady == TRUE | Flag_MOCSStartCmd == TRUE Flag_FOSPumpUnitStat == FALSE | Flag_MOCSStartCmd == or(Flag_GE#MOCSStartCmd) FO Pump Auto 동작 불가(Yard에서 Pump 제어하는 경우 제외)

## No#.HD
IDX | Alarm Tag | Enable | HW Tag | System Unit | Message | Min | Max | Unit | Threshold | Delay | Not Ready | Action | Alarm State | Reset Button | Alarm Reset Condition | Remark
double | string | string | string | string | string | double | double | string | string | double | string | string | string | string | string | string
0 | No#_DI1_MF | O | #DI1 | Module | No.# DI1 Module Fault | 0 | 1 | - | 1 | 0.1 | X |  | All | X
1 | No#_DO1_MF | O | #DO1 | Module | No.# DO1 Module Fault | 0 | 1 | - | 1 | 0.1 | X |  | All | X
2 | No#_AI1_MF | O | #AI1 | Module | No.# AI1 Module Fault | 0 | 1 | - | 1 | 0.1 | X |  | All | X
3 | No#_AI2_MF | O | #AI2 | Module | No.# AI2 Module Fault | 0 | 1 | - | 1 | 0.1 | X |  | All | X
4 | No#_AI3_MF | O | #AI3 | Module | No.# AI3 Module Fault | 0 | 1 | - | 1 | 0.1 | X |  | All | X
5 | No#_AO1_MF | O | #AO1 | Module | No.# AO1 Module Fault | 0 | 1 | - | 1 | 0.1 | X |  | All | X
6 | No#_ENG10-70#_DH | X | ENG10-70# |  | #DI1 CH1 Reserved High(High=Close) | 0 | 1 | - | 1 | 1 |  |  | All
7 | No#_ENG10-70#_DL | X | ENG10-70# |  | #DI1 CH1 Reserved Low(High=Close) | 0 | 1 | - | 0 | 1 | O | MOCS Shutdown | MOCS Engage MOCS Active | O
8 | No#_MOC00-20#_DH | X | MOC00-20# | MOCS | No.# MOCS Remote/Local High(High=Remote) | 0 | 1 | - | 1 | 0.1 |  |  | All
9 | No#_MOC00-20#_DL | X | MOC00-20# | MOCS | No.# MOCS Remote/Local Low(High=Remote) | 0 | 1 | - | 0 | 0.1 |  |  | All
10 | No#_MOC00-91#P_DH | X | MOC00-91#P | MOCS | No.# MOCS Em'cy stop From panel (To module) High(Low=Em'cy Stop) | 0 | 1 | - | 1 | 0.1 |  |  | All
11 | No#_MOC00-91#P_DL | O | MOC00-91#P | MOCS | No.# MOCS Em'cy stop From panel (To module) Low(Low=Em'cy Stop) | 0 | 1 | - | 0 | 0.1 | O | Valve Shutdown | All | O
12 | No#_MOC00-91#E_DH | X | MOC00-91#E | MOCS | No.# MOCS Em'cy stop From ECR (To module) High(Low=Em'cy Stop) | 0 | 1 | - | 1 | 0.1 |  |  | All
13 | No#_MOC00-91#E_DL | O | MOC00-91#E | MOCS | No.# MOCS Em'cy stop From ECR (To module) Low(Low=Em'cy Stop) | 0 | 1 | - | 0 | 0.1 | O | Valve Shutdown | All | O
14 | No#_MOC00-91#B_DH | X | MOC00-91#B | MOCS | No.# MOCS Em'cy stop From Bridge (To module) High(Low=Em'cy Stop) | 0 | 1 | - | 1 | 0.1 |  |  | All
15 | No#_MOC00-91#B_DL | O | MOC00-91#B | MOCS | No.# MOCS Em'cy stop From Bridge (To module) Low(Low=Em'cy Stop) | 0 | 1 | - | 0 | 0.1 | O | Valve Shutdown | All | O
16 | No#_MOC10-11#_DH | X | MOC10-11# | MOCS | No.# MOCS Start High(High=Start) | 0 | 1 | - | 1 | 0.1 |  |  | All
17 | No#_MOC10-11#_DL | X | MOC10-11# | MOCS | No.# MOCS Start Low(High=Start) | 0 | 1 | - | 0 | 0.1 |  |  | All
18 | No#_BV10-11#_DH | X | BV10-11# | MOCS | No.# MOCS Preparation High(High=Preparation) | 0 | 1 | - | 1 | 0.1 |  |  | All
19 | No#_BV10-11#_DL | X | BV10-11# | MOCS | No.# MOCS Preparation Low(High=Preparation) | 0 | 1 | - | 0 | 0.1 |  |  | All
20 | No#_MOC10-01#_DH | X | MOC10-01# | MOCS | No.# MOCS Stop High(High=Stop) | 0 | 1 | - | 1 | 0.1 |  |  | All
21 | No#_MOC10-01#_DL | X | MOC10-01# | MOCS | No.# MOCS Stop Low(High=Stop) | 0 | 1 | - | 0 | 0.1 |  |  | All
22 | No#_XC104#01-2_DH | X | XC104#01-2 | MOCS | No.# RSV Feedback(Open) High(High=Open) | 0 | 1 | - | 1 | 0.1 |  |  | All |  |  | RSV Feedback Alarm is defined on sheet No#.UD
23 | No#_XC104#01-2_DL | X | XC104#01-2 | MOCS | No.# RSV Feedback(Open) Low(High=Open) | 0 | 1 | - | 0 | 0.1 |  |  | All |  |  | RSV Feedback Alarm is defined on sheet No#.UD
24 | No#_XC104#01-3_DH | X | XC104#01-3 | MOCS | No.# RSV Feedback(Closed) High(High=Close) | 0 | 1 | - | 1 | 0.1 |  |  | All |  |  | RSV Feedback Alarm is defined on sheet No#.UD
25 | No#_XC104#01-3_DL | X | XC104#01-3 | MOCS | No.# RSV Feedback(Closed) Low(High=Close) | 0 | 1 | - | 0 | 0.1 |  |  | All |  |  | RSV Feedback Alarm is defined on sheet No#.UD
26 | No#_XC104#02-2_DH | X | XC104#02-2 | MOCS | No.# RBV Feedback(Open) High(High=Open) | 0 | 1 | - | 1 | 0.1 |  |  | All |  |  | RBV Feedback Alarm is defined on sheet No#.UD
27 | No#_XC104#02-2_DL | X | XC104#02-2 | MOCS | No.# RBV Feedback(Open) Low(High=Open) | 0 | 1 | - | 0 | 0.1 |  |  | All |  |  | RBV Feedback Alarm is defined on sheet No#.UD
28 | No#_XC104#02-3_DH | X | XC104#02-3 | MOCS | No.# RBV Feedback(Closed) High(High=Close) | 0 | 1 | - | 1 | 0.1 |  |  | All |  |  | RBV Feedback Alarm is defined on sheet No#.UD
29 | No#_XC104#02-3_DL | X | XC104#02-3 | MOCS | No.# RBV Feedback(Closed) Low(High=Close) | 0 | 1 | - | 0 | 0.1 |  |  | All |  |  | RBV Feedback Alarm is defined on sheet No#.UD
30 | No#_TS103#42_DH | X | TS103#42 | FODS | No.# F.O. Dosing Fuel Oil Inlet Temp High(Low = 60℃ 이상) | 0 | 1 | - | 1 | 1 |  |  | All
31 | No#_TS103#42_DL | O | TS103#42 | FODS | No.# F.O. Dosing Fuel Oil Inlet Temp Low(Low = 60℃ 이상) | 0 | 1 | - | 0 | 1 | O | Disengage | All
32 |  | X |  |  | #DI1 CH14 Reserved High(High=Close) | 0 | 1 | - | 1 | 0.1 |  |  | All |  |  | SCR VV Feedback Alarm is defined on sheet No#.UD
33 |  | X |  |  | #DI1 CH14 Reserved Low(High=Close) | 0 | 1 | - | 0 | 0.1 |  |  | All |  |  | SCR VV Feedback Alarm is defined on sheet No#.UD
34 |  | X |  |  | #DI1 CH15 Reserved High(High=Close) | 0 | 1 | - | 1 | 0.1 |  |  | All |  |  | SCR VV Feedback Alarm is defined on sheet No#.UD
35 |  | X |  |  | #DI1 CH15 Reserved Low(High=Close) | 0 | 1 | - | 0 | 0.1 |  |  | All |  |  | SCR VV Feedback Alarm is defined on sheet No#.UD
36 |  | X |  |  | #DI1 CH16 Reserved High(High=Close) | 0 | 1 | - | 1 | 0.1 |  |  | All
37 |  | X |  |  | #DI1 CH16 Reserved Low(High=Close) | 0 | 1 | - | 0 | 0.1 |  |  | All
38 | No#_TC106#40_SF | O | TC106#40 | MOCS | No.# MOCS Injection pipe Inlet Temp S/F | 0 | 600 | °C | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
39 | No#_TC106#40_LL | X | TC106#40 | MOCS | No.# MOCS Injection pipe Inlet Temp Low-Low | 0 | 600 | °C | 0 | 1 |  |  | All
40 | No#_TC106#40_LO | X | TC106#40 | MOCS | No.# MOCS Injection pipe Inlet Temp Low | 0 | 600 | °C | 0 | 1 |  |  | All
41 | No#_TC106#40_HO | X | TC106#40 | MOCS | No.# MOCS Injection pipe Inlet Temp High | 0 | 600 | °C | 0 | 1 |  |  | All
42 | No#_TC106#40_HH | X | TC106#40 | MOCS | No.# MOCS Injection pipe Inlet Temp High-High | 0 | 600 | °C | 0 | 1 |  |  | All
43 | No#_TC107#40_SF | O | TC107#40 | MOCS | No.# Chamber Inlet Temp S/F | 0 | 800 | °C | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
44 | No#_TC107#40_LL | O | TC107#40 | MOCS | No.# Chamber Inlet Temp Low-Low | 0 | 800 | °C | 280 | 10 |  | MOCS Shutdown | MOCS Active |  | !(MOCS Active)
45 | No#_TC107#40_LO | O | TC107#40 | MOCS | No.# Chamber Inlet Temp Low | 0 | 800 | °C | 290 | 10 |  |  | MOCS Active |  | !(MOCS Active)
46 | No#_TC107#40_HO | O | TC107#40 | MOCS | No.# Chamber Inlet Temp High | 0 | 800 | °C | 480 | 10 |  |  | All
47 | No#_TC107#40_HH | O | TC107#40 | MOCS | No.# Chamber Inlet Temp High-High | 0 | 800 | °C | 500 | 60 |  | MOCS Shutdown | All
48 | No#_TC107#41_SF | O | TC107#41 | MOCS | No.# Chamber Middle Temp S/F | 0 | 800 | °C | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
49 | No#_TC107#41_LL | O | TC107#41 | MOCS | No.# Chamber Middle Temp Low-Low | 0 | 800 | °C | 280 | 10 |  | MOCS Shutdown | MOCS Active |  | !(MOCS Active)
50 | No#_TC107#41_LO | O | TC107#41 | MOCS | No.# Chamber Middle Temp Low | 0 | 800 | °C | 290 | 10 |  |  | MOCS Active |  | !(MOCS Active)
51 | No#_TC107#41_HO | O | TC107#41 | MOCS | No.# Chamber Middle Temp High | 0 | 800 | °C | 500 | 10 |  |  | All
52 | No#_TC107#41_HH | O | TC107#41 | MOCS | No.# Chamber Middle Temp High-High | 0 | 800 | °C | 520 | 1 |  | MOCS Shutdown | All
53 | No#_TC107#42_SF | O | TC107#42 | MOCS | No.# Chamber Outlet Temp S/F | 0 | 800 | °C | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
54 | No#_TC107#42_LL | O | TC107#42 | MOCS | No.# Chamber Outlet Temp Low-Low | 0 | 800 | °C | 280 | 10 |  | MOCS Shutdown | MOCS Active |  | !(MOCS Active)
55 | No#_TC107#42_LO | O | TC107#42 | MOCS | No.# Chamber Outlet Temp Low | 0 | 800 | °C | 290 | 10 |  |  | MOCS Active |  | !(MOCS Active)
56 | No#_TC107#42_HO | O | TC107#42 | MOCS | No.# Chamber Outlet Temp High | 0 | 800 | °C | 580 | 10 |  |  | All
57 | No#_TC107#42_HH | O | TC107#42 | MOCS | No.# Chamber Outlet Temp High-High | 0 | 800 | °C | 600 | 1 |  | MOCS Shutdown | All
58 | No#_PDT107#43_SF | O | PDT107#43 | MOCS | No.# Chamber Diff. Press S/F | 0 | 100 | mbar | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
59 | No#_PDT107#43_LL | X | PDT107#43 | MOCS | No.# Chamber Diff. Press Low-Low | 0 | 100 | mbar | 0 | 1 |  |  | All
60 | No#_PDT107#43_LO | O | PDT107#43 | MOCS | No.# Chamber Diff. Press Low | 0 | 100 | mbar | 0.5 | 300 | O | Disengage | All |  |  | 촉매 확인용, 시험중엔 Disenable
61 | No#_PDT107#43_HO | O | PDT107#43 | MOCS | No.# Chamber Diff. Press High | 0 | 100 | mbar | 20 | 60 |  |  | All
62 | No#_PDT107#43_HH | O | PDT107#43 | MOCS | No.# Chamber Diff. Press High-High | 0 | 100 | mbar | 24 | 60 | O | Disengage | All
63 | No#_PT105#50_SF | O | PT105#50 | MOCS | No.# Venting & Sealing Air Inlet Press S/F | 0 | 16 | bar | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA Sealing->Init: 반영하지 않기로 함
64 | No#_PT105#50_LL | O | PT105#50 | MOCS | No.# Venting & Sealing Air Inlet Press Low-Low | 0 | 16 | bar | 3.5 | 5 |  |  | All |  |  | Sealing->Init: 반영하지 않기로 함
65 | No#_PT105#50_LO | O | PT105#50 | MOCS | No.# Venting & Sealing Air Inlet Press Low | 0 | 16 | bar | 4 | 5 |  |  | All
66 | No#_PT115#50_HO | O | PT105#50 | MOCS | No.# Venting & Sealing Air Inlet Press High | 0 | 16 | bar | 7.5 | 5 |  |  | All
67 | No#_PT105#50_HH | O | PT105#50 | MOCS | No.# Venting & Sealing Air Inlet Press High-High | 0 | 16 | bar | 8 | 5 |  |  | All |  |  | Sealing->Init: 반영하지 않기로 함
68 | No#_#AI1CH7_SF | X |  |  | #AI1 CH7 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
69 | No#_#AI1CH7_LL | X |  |  | #AI1 CH7 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
70 | No#_#AI1CH7_LO | X |  |  | #AI1 CH7 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
71 | No#_#AI1CH7_HO | X |  |  | #AI1 CH7 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
72 | No#_#AI1CH7_HH | X |  |  | #AI1 CH7 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
73 | No#_#AI1CH8_SF | X |  |  | #AI1 CH8 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
74 | No#_#AI1CH8_LL | X |  |  | #AI1 CH8 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
75 | No#_#AI1CH8_LO | X |  |  | #AI1 CH8 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
76 | No#_#AI1CH8_HO | X |  |  | #AI1 CH8 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
77 | No#_#AI1CH8_HH | X |  |  | #AI1 CH8 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
78 |  | X |  |  | #AI2 CH1 Reserved S/F | 0 | 100 | mbar | 0 | 1 | O | MOCS Shutdown | All |  |  | S/F: below 3.2mA, above 20.8mA
79 |  | X |  |  | #AI2 CH1 Reserved Low-Low | 0 | 100 | mbar | 0 | 1 |  |  | All
80 |  | X |  |  | #AI2 CH1 Reserved Low | 0 | 100 | mbar | 0 | 1 |  |  | All
81 |  | X |  |  | #AI2 CH1 Reserved High | 0 | 100 | mbar | 40 | 5 |  |  | All
82 |  | X |  |  | #AI2 CH1 Reserved High-High | 0 | 100 | mbar | 44 | 1 | O | MOCS Shutdown | All
83 | No#_PDT104#42_SF | X | PDT104#42 | MOCS | No.# RTV Diff. Press S/F | 0 | 100 | mbar | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA No.# RTV PDT S/F Alarm @Sealing is defined on sheet No#.UD
84 | No#_PDT104#42_LL | X | PDT104#42 | MOCS | No.# RTV Diff. Press Low-Low | 0 | 100 | mbar | 0 | 1 |  |  | All
85 | No#_PDT104#42_LO | O | PDT104#42 | MOCS | No.# RTV Diff. Press Low | 0 | 100 | mbar | 3 | 60 |  |  | Sealing |  |  | Sealing 이후, 10분(DELAY_PDT_LOW) 뒤 부터 Alarm 활성화
86 | No#_PDT104#42_HO | O | PDT104#42 | MOCS | No.# RTV Diff. Press High | 0 | 100 | mbar | 50 | 1 |  |  | Sealing
87 | No#_PDT104#42_HH | O | PDT104#42 | MOCS | No.# RTV Diff. Press High-High | 0 | 100 | mbar | 70 | 5 |  |  | Sealing |  |  | Sealing State 유지, Open RTV 100% 10s
88 | No#_XC104#03-2_SF | O | XC104#03-2 | MOCS | No.# RTV Feedback S/F | 0 | 100 | % | 0 | 1 | O | Valve Shutdown | All | O |  | S/F: below 3.2mA, above 20.8mA
89 | No#_XC104#03-2_LL | X | XC104#03-2 | MOCS | No.# RTV Feedback Low-Low | 0 | 100 | % | 0 | 1 |  |  | All |  |  | RTV Feedback Alarm is defined on sheet No#.UD
90 | No#_XC104#03-2_LO | X | XC104#03-2 | MOCS | No.# RTV Feedback Low | 0 | 100 | % | 0 | 1 |  |  | All |  |  | RTV Feedback Alarm is defined on sheet No#.UD
91 | No#_XC104#03-2_HO | X | XC104#03-2 | MOCS | No.# RTV Feedback High | 0 | 100 | % | 0 | 1 |  |  | All |  |  | RTV Feedback Alarm is defined on sheet No#.UD
92 | No#_XC104#03-2_HH | X | XC104#03-2 | MOCS | No.# RTV Feedback High-High | 0 | 100 | % | 10 | 60 |  |  | All |  |  | RTV Feedback Alarm is defined on sheet No#.UD
93 | No#_#AI2CH4_SF | X |  |  | #AI2 CH4 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
94 | No#_#AI2CH4_LL | X |  |  | #AI2 CH4 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
95 | No#_#AI2CH4_LO | X |  |  | #AI2 CH4 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
96 | No#_#AI2CH4_HO | X |  |  | #AI2 CH4 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
97 | No#_#AI2CH4_HH | X |  |  | #AI2 CH4 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
98 | No#_#AI2CH5_SF | X |  |  | #AI2 CH5 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
99 | No#_#AI2CH5_LL | X |  |  | #AI2 CH5 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
100 | No#_#AI2CH5_LO | X |  |  | #AI2 CH5 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
101 | No#_#AI2CH5_HO | X |  |  | #AI2 CH5 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
102 | No#_#AI2CH5_HH | X |  |  | #AI2 CH5 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
103 | No#_#AI2CH6_SF | X |  |  | #AI2 CH6 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
104 | No#_#AI2CH6_LL | X |  |  | #AI2 CH6 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
105 | No#_#AI2CH6_LO | X |  |  | #AI2 CH6 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
106 | No#_#AI2CH6_HO | X |  |  | #AI2 CH6 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
107 | No#_#AI2CH6_HH | X |  |  | #AI2 CH6 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
108 | No#_#AI2CH7_SF | X |  |  | #AI2 CH7 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
109 | No#_#AI2CH7_LL | X |  |  | #AI2 CH7 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
110 | No#_#AI2CH7_LO | X |  |  | #AI2 CH7 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
111 | No#_#AI2CH7_HO | X |  |  | #AI2 CH7 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
112 | No#_#AI2CH7_HH | X |  |  | #AI2 CH7 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
113 | No#_#AI2CH8_SF | X |  |  | #AI2 CH8 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
114 | No#_#AI2CH8_LL | X |  |  | #AI2 CH8 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
115 | No#_#AI2CH8_LO | X |  |  | #AI2 CH8 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
116 | No#_#AI2CH8_HO | X |  |  | #AI2 CH8 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
117 | No#_#AI2CH8_HH | X |  |  | #AI2 CH8 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
118 | No#_PT103#40_SF | O | PT103#40 | FODS | No.# F.O. Dosing Atomizing Air Inlet Press S/F | 0 | 10 | bar | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
119 | No#_PT103#40_LL | O | PT103#40 | FODS | No.# F.O. Dosing Atomizing Air Inlet Press Low-Low | 0 | 10 | bar | 3.5 | 5 | O | Disengage | FODS Cooling FODS Dosing FODS Flushing
120 | No#_PT103#40_LO | O | PT103#40 | FODS | No.# F.O. Dosing Atomizing Air Inlet Press Low | 0 | 10 | bar | 4 | 5 |  |  | FODS Cooling FODS Dosing FODS Flushing
121 | No#_PT103#40_HO | X | PT103#40 | FODS | No.# F.O. Dosing Atomizing Air Inlet Press High | 0 | 10 | bar | 0 | 1 |  |  | All
122 | No#_PT103#40_HH | X | PT103#40 | FODS | No.# F.O. Dosing Atomizing Air Inlet Press High-High | 0 | 10 | bar | 0 | 1 |  |  | All
123 | No#_PT103#41_SF | O | PT103#41 | FODS | No.# F.O. Dosing Atomizing Air Outlet Press S/F | 0 | 10 | bar | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
124 | No#_PT103#41_LL | O | PT103#41 | FODS | No.# F.O. Dosing Atomizing Air Outlet Press Low-Low | 0 | 10 | bar | 1 | 5 |  | Disengage | FODS Cooling FODS Dosing FODS Flushing
125 | No#_PT103#41_LO | O | PT103#41 | FODS | No.# F.O. Dosing Atomizing Air Outlet Press Low | 0 | 10 | bar | 3 | 5 |  |  | FODS Cooling FODS Dosing FODS Flushing
126 | No#_PT103#41_HO | X | PT103#41 | FODS | No.# F.O. Dosing Atomizing Air Outlet Press High | 0 | 10 | bar | 0 | 1 |  |  | All
127 | No#_PT103#41_HH | X | PT103#41 | FODS | No.# F.O. Dosing Atomizing Air Outlet Press High-High | 0 | 10 | bar | 0 | 1 |  |  | All
128 | No#_PT103#43_SF | O | PT103#43 | FODS | No.# F.O. Dosing Fuel Oil Inlet Press S/F | 0 | 16 | bar | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
129 | No#_PT103#43_LL | O | PT103#43 | FODS | No.# F.O. Dosing Fuel Oil Inlet Press Low-Low | 0 | 16 | bar | 4 | 5 |  | Disengage | F.O. Supply Pump Running
130 | No#_PT103#43_LO | O | PT103#43 | FODS | No.# F.O. Dosing Fuel Oil Inlet Press Low | 0 | 16 | bar | 5 | 2 |  |  | F.O. Supply Pump Running
131 | No#_PT103#43_HO | O | PT103#43 | FODS | No.# F.O. Dosing Fuel Oil Inlet Press High | 0 | 16 | bar | 10 | 10 |  |  | All
132 | No#_PT103#43_HH | O | PT103#43 | FODS | No.# F.O. Dosing Fuel Oil Inlet Press High-High | 0 | 16 | bar | 11 | 1 |  | Disengage | All
133 | No#_PT103#44_SF | O | PT103#44 | FODS | No.# F.O. Dosing Fuel Oil Middle Press S/F | 0 | 16 | bar | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
134 | No#_PT103#44_LL | O | PT103#44 | FODS | No.# F.O. Dosing Fuel Oil Middle Press Low-Low | 0 | 16 | bar | 4 | 5 |  | Disengage | F.O. Supply Pump Running F.O. In/Out Sol. VV Open
135 | No#_PT103#44_LO | O | PT103#44 | FODS | No.# F.O. Dosing Fuel Oil Middle Press Low | 0 | 16 | bar | 5 | 5 |  |  | F.O. Supply Pump Running F.O. In/Out Sol. VV Open |  |  | Regulator 고장
136 | No#_PT103#44_HO | X | PT103#44 | FODS | No.# F.O. Dosing Fuel Oil Middle Press High | 0 | 16 | bar | 0 | 1 |  |  | All
137 | No#_PT103#44_HH | X | PT103#44 | FODS | No.# F.O. Dosing Fuel Oil Middle Press High-High | 0 | 16 | bar | 0 | 1 |  |  | All
138 | No#_FT103#45-2_SF | O | FT103#45-2 | FODS | No.# F.O. Dosing Fuel Oil Flowrate (Feedback) S/F | 0 | 100 | L/h | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
139 | No#_FT103#45-2_LL | X | FT103#45-2 | FODS | No.# F.O. Dosing Fuel Oil Flowrate (Feedback) Low-Low | 0 | 100 | L/h | 0 | 1 |  |  | All
140 | No#_FT103#45-2_LO | X | FT103#45-2 | FODS | No.# F.O. Dosing Fuel Oil Flowrate (Feedback) Low | 0 | 100 | L/h | 0 | 1 |  |  | All
141 | No#_FT103#45-2_HO | O | FT103#45-2 | FODS | No.# F.O. Dosing Fuel Oil Flowrate (Feedback) High | 0 | 100 | L/h | Ref x 155% | 100 |  |  | All |  |  | Ref: Ref F.O. flowrate setpoint
142 | No#_FT103#45-2_HH | O | FT103#45-2 | FODS | No.# F.O. Dosing Fuel Oil Flowrate (Feedback) High-High | 0 | 100 | L/h | Ref x 160% | 10 |  |  | All |  |  | Ref: Ref F.O. flowrate setpoint
143 | No#_PT103#47_SF | O | PT103#47 | FODS | No.# F.O. Dosing Fuel Oil Outlet Press S/F | 0 | 16 | bar | 0 | 1 | O | Disengage | All |  |  | S/F: below 3.2mA, above 20.8mA
144 | No#_PT103#47_LL | O | PT103#47 | FODS | No.# F.O. Dosing Fuel Oil Outlet Press Low-Low | 0 | 16 | bar | 0.5 | 5 |  | Disengage | F.O. Supply Pump Running F.O. In/Out Sol. VV Open F.O. Ctrl. VV > 0%
145 | No#_PT103#47_LO | O | PT103#47 | FODS | No.# F.O. Dosing Fuel Oil Outlet Press Low | 0 | 16 | bar | 1 | 2 |  |  | F.O. Supply Pump Running F.O. In/Out Sol. VV Open F.O. Ctrl. VV > 0%
146 | No#_PT103#47_HO | X | PT103#47 | FODS | No.# F.O. Dosing Fuel Oil Outlet Press High | 0 | 16 | bar | 0 | 1 |  |  | All
147 | No#_PT103#47_HH | X | PT103#47 | FODS | No.# F.O. Dosing Fuel Oil Outlet Press High-High | 0 | 16 | bar | 0 | 1 |  |  | All
148 | No#_#AI3CH7_SF | X |  |  | #AI3 CH7 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
149 | No#_#AI3CH7_LL | X |  |  | #AI3 CH7 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
150 | No#_#AI3CH7_LO | X |  |  | #AI3 CH7 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
151 | No#_#AI3CH7_HO | X |  |  | #AI3 CH7 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
152 | No#_#AI3CH7_HH | X |  |  | #AI3 CH7 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All
153 | No#_#AI3CH8_SF | X |  |  | #AI3 CH8 Reserved S/F | 0 | 1 | - | 0 | 1 |  |  | All |  |  | S/F: below 3.2mA, above 20.8mA
154 | No#_#AI3CH8_LL | X |  |  | #AI3 CH8 Reserved Low-Low | 0 | 1 | - | 0 | 1 |  |  | All
155 | No#_#AI3CH8_LO | X |  |  | #AI3 CH8 Reserved Low | 0 | 1 | - | 0 | 1 |  |  | All
156 | No#_#AI3CH8_HO | X |  |  | #AI3 CH8 Reserved High | 0 | 1 | - | 0 | 1 |  |  | All
157 | No#_#AI3CH8_HH | X |  |  | #AI3 CH8 Reserved High-High | 0 | 1 | - | 0 | 1 |  |  | All

## No#.UD
IDX | Alarm Tag | Enable | HW Tag | System Unit | Message | Min | Max | Unit | Threshold | Delay | Not Ready | Action | Alarm State | Reset Button | Alarm Reset Condition | Flag | Remark
double | string | string | string | string | string | double | double | string | string | double | string | string | string | string | string | string | string
0 | NO#_COMMGE_FL | O |  | MOCS | Communication Fail between No.# Engine and AMS | 0 | 1 | - | 0 | 1 | O | MOCS Shutdown | All |  |  | AMS_GE#Comm == FALSE | Communication between No.# engine and AMS is not verified
3 | NO#_DIESEL_FL | O |  | MOCS | No.# Engine Sudden Diesel Transfer | 0 | 1 | - | 0 | 0.1 | O | MOCS Shutdown | MOCS Engage MOCS Active MOCS Disengage | O |  | AMS_GE#GT == TRUE AMS_GE#PT == TRUE AMS_GE#GasFuel == TRUE | ENGINE_GAS_TRIP > 0 ENGINE_PILOT_TRIP > 0 FUEL_MODE = 3 or 5
4 | NO#_EGSTOP_FL | O |  | MOCS | No.# Engine Stop During Gas Operation | 0 | 1 | - | 0 | 0.1 | O | MOCS Shutdown | All | O |  | AMS_GE#SD == TRUE | Engine Shutdown(Gas mode), Stop(Gas mode)
5 | NO#_MSSFAIL_FL | O |  | MOCS | No.# MSS Normal Fail | 0 | 1 | - | 0 | 0.1 | O | MOCS Shutdown | TMB Bypass TMB Sealing | O |  | Flag_GE#MSSNormal == False | Timer(MSS Normal Flag False) > [TMB Time out Threshold](Control Paramter)
6 | NO#_TMBTO_FL | O |  | MOCS | No.# TMB Time out | 0 | 1 | - | 0 | 0.1 | O | MOCS Shutdown | TMB Bypass TMB Sealing | O |  | Flag_GE#TMB == TRUE | Timer(TMB Flag True) > [TMB Time out Threshold](Control Paramter)
7 | NO#_STOPTMB_FL | O |  | MOCS | No.# Remote Stop Command Input while TMB State(except TMB Engage) | 0 | 1 | - | 0 | 0.1 | X | MOCS Shutdown | TMB Bypass TMB Sealing | O |  |  | When the MOCS Remote stop button is pressed while in TMB Bypass/Sealing State
8 | NO#_NREADY_FL | X |  | MOCS | No.# MOCS Not Ready | 0 | 1 | - | 0 | 0.1 |  |  | Init Sealing |  | MOCS Ready Flag == TRUE |  | When the MOCS Remote start button is pressed when MOCS Ready Flag == False
9 | NO#_RSVFA_FL | O | XC104#01-3 | MOCS | No.# RSV Fail | 0 | 1 | - | 0 | 10 | O | Valve Shutdown | All | O |  |  | Command(Open/Close) ≠ Status(Feedback 신호로 판단, Open/Close/Transfer)
10 | NO#_RSVSF_FL | O | XC104#01-3 | MOCS | No.# RSV Feedback S/F | 0 | 1 | - | 0 | 1 | O | Valve Shutdown | All | O |  |  | (Open Feedback = TRUE) & (Close Feedback = TRUE)
11 | NO#_RBVFA_FL | O | XC104#02-2 | MOCS | No.# RBV Fail | 0 | 1 | - | 0 | 10 | O | Valve Shutdown | All | O |  |  | Command(Open/Close) ≠ Status(Feedback 신호로 판단, Open/Close/Transfer)
12 | NO#_RBVSF_FL | O | XC104#02-2 | MOCS | No.# RBV Feedback S/F | 0 | 1 | - | 0 | 1 | O | Valve Shutdown | All | O |  |  | (Open Feedback = TRUE) & (Close Feedback = TRUE)
13 | NO#_SCRVVFA_FL | X | XC104#04-2 | MOCS | No.# SCR Valve Fail | 0 | 1 | - | 0 | 10 | O | Valve Shutdown | All | O |  |  | Command(Open/Close) ≠ Status(Feedback 신호로 판단, Open/Close/Transfer)
14 | NO#_SCRVVSF_FL | X | XC104#04-2 | MOCS | No.# SCR Valve Feedback S/F | 0 | 1 | - | 0 | 1 | O | Valve Shutdown | All | O |  |  | (Open Feedback = TRUE) & (Close Feedback = TRUE)
15 | NO#_RTVFA_ED | O | XC104#03-2 | MOCS | No.# RTV Fail | 0 | 100 | % | 10 | 60 | O | Valve Shutdown | All | O |  |  | ¦reference input - valve feedback¦ >= Threshold
16 | NO#_RTVDEV_ED | O | XC104#03-3 | MOCS | No.# RTV Deviation | 0 | 100 | % | 2 | 180 | O | Valve Shutdown | All | O |  |  | ¦reference input - valve feedback¦ >= Threshold
17 | NO#_DFODEV_ED | O | FT103#45-2 | FODS | No.# Dosing F.O. Flow Deviation | 0 | 100 | % | 5 | 120 |  |  | FODS Dosing & Engine Steady State |  |  |  | (¦QF.O. Feedback - QF.O. Setpoint¦ / QF.O. Setpoint) * 100 >= Threshold
18 | NO#_DFODEVTO_FL | O | FT103#45-2 | FODS | No.# Dosing F.O. Flow Deviation Time out | 0 | 1 | - | 0 | 600 |  | Disengage | FODS Dosing & Engine Steady State |  |  |  | Timer(NO#_DFODEV_ED Alarm) >= Thershold
19 | NO#_DFOSAT_FL | O | FT103#45-2 | FODS | No.# Dosing F.O. Limit Saturation Time out | 0 | 1 | - | 0 | 3600 |  | Disengage | FODS Dosing |  |  |  | Timer(QF.O. Setpoint = QF.O. High Limit) >= Thershold
20 | NO#_RTVPDTSF_FL | O | PDT104#42 | MOCS | No.# RTV PDT S/F MOCS Not ready - Sealing required | 0 | 100 | mbar | 0 | 1 |  | Init | MOCS Init MOCS Sealing |  |  |  | S/F: below 3.2mA, above 20.8mA No.# RTV PDT S/F Alarm @All state is defined on sheet No#.HD
22 | NO#_NRDGAS_FL | O |  | MOCS | No.# MOCS Not Ready - Wating Gas Operation | 0 | 1 | - | 0 | 0.1 | O |  | Init Sealing |  | Flag_MOCSReady == TRUE | Flag_MOCSStartCmd == TRUE AMS_GE#GasFuel == TRUE | Flag_MOCSStartCmd == or(Flag_GE#MOCSStartCmd)
23 | NO#_NRDMSS_FL | O |  | MOCS | No.# MOCS Not Ready - Wating MSS Normal Condition | 0 | 1 | - | 0 | 0.1 | O |  | Init Sealing |  | Flag_MOCSReady == TRUE | Flag_MOCSStartCmd == TRUE Flag_MSSNormal == FALSE | Flag_MOCSStartCmd == or(Flag_GE#MOCSStartCmd)
24 | NO#_NRDSTB_FL | O |  | MOCS | No.# MOCS Not Ready - Waiting for engine stabilization | 0 | 1 | - | 0 | 0.1 | O |  | Init Sealing |  | Flag_MOCSReady == TRUE | Flag_MOCSStartCmd == TRUE Flag_GE#EGSTB == FALSE | Flag_MOCSStartCmd == or(Flag_GE#MOCSStartCmd)
| NO#_STLIFE30_FL | O |  | MOCS | No.# S-trap lifetime remaining: below 30% | 0 | 1 | - | 0 | 0.1 |  |  | All |  | Flag_StrapLife30Ack == TRUE | Flag_StrapLife30Ack == FALSE StrapLifetime <= 30
| NO#_STLIFE10_FL | O |  | MOCS | No.# S-trap lifetime remaining: below 10% | 0 | 1 | - | 0 | 0.1 |  |  | All |  | Flag_StrapLife10Ack == TRUE | Flag_StrapLife10Ack == FALSE StrapLifetime <= 10
NO#_
NO#_
NO#_
NO#_
NO#_
NO#_